## Sheet1
Attack # | Start Time | End Time | Attack Point | Start State | Attack | Actual Change | Expected Impact or attacker intent | Unexpected Outcome
0 | 2015-12-28 10:29 | 10:45 | MV-101 | MV-101 is closed | Open MV-101 | Yes | Tank overflow
1 | 2015-12-28 10:51 | 10:58 | P-102 | P-101 is on where as P-102 is off | Turn on P-102 | Yes | Pipe bursts
2 | 2015-12-28 11:22 | 11:28 | LIT-101 | Water level between L and H | Increase by 1 mm every second | No | Tank Underflow; Damage P-101
3 | 2015-12-28 11:48 | 11:54 | MV-504 | MV-504 is closed | Open MV-504 | Yes | Halt RO shut down sequence; Reduce life of RO | No impact
4 | 2015-12-28 12:01 | 12:04 | AIT-202 | Value of AIT-202 is >7.05 | Set value of AIT-202 as 6 | No | P-203 turns off; Change in water quality | Impact seen on AIT-504 after two hours at around 14:15. It increased above HH but Drainage did not start
5 | 2015-12-28 12:08 | 12:16 | LIT-301 | Water level between L and H | Water level increased above HH | No | Stop of inflow; Tank underflow; Damage P-301
6 | 2015-12-28 13:10 | 13:26 | DPIT-301 | Value of DPIT is <40kpa | Set value of DPIT as >40kpa | No | Backwash process is started again and again; Normal operation stops; Decrease in water level of tank 401. Increase in water level of tank 301
7 | 2015-12-28 14:16 | 14:19 | FIT-401 | Value of FIT-401 above 1 | Set value of FIT-401 as <0.7 | No | UV shutdown; P-501 turns off; | UV did not shutdown; P-501 did not turn off
8 | 2015-12-28 14:19 | 14:28 | FIT-401 | Value of FIT-401 above 1 | Set value of FIT-401 as 0 | No | UV shutdown; P-501 turns off;
9 | 2015-12-29 11:11 | 11:15 | MV-304 | MV-304 is open | Close MV-304 | Yes | Halt of stage 3 because change in the backwash process | UF Startup did not stop because MV-304 was closed late
10 | 2015-12-29 11:36 | 11:43 | Mv-303 | MV-303 is closed | Do not let MV-303 open | Yes | Halt of stage 3 because change in the backwash process | Attack Failed because Startup sequence did not start because Tank 301 was already full
11 | 2015-12-29 11:57 | 12:02 | LIT-301 | Water level between L and H | Decrease water level by 1mm each second | No | Tank Overflow
12 | 2015-12-29 14:38 | 14:50 | MV-303 | Closed | Do not let MV-303 open | Yes | Halt of stage 3 because change in the backwash process
13 | 2015-12-29 18:11 | 18:15 | AIT-504 | Value of AIT-504 <15 uS/cm | Set value of AIT-504 to 16 uS/cm | No | RO shut down sequence starts after 30 minutes. Water should go to drain. | RO did not shutdown; Water did not go to drain
14 | 2015-12-29 18:16 | 18:22 | AIT-504 | Value of AIT-504 <15 uS/cm | Set value of AIT-504 to 255 uS/cm | No | RO shut down sequence starts after 30 minutes. Water should go to drain. | RO did not shutdown; Water did not go to drain
15 | 2015-12-29 18:30 | 18:42 | MV-101, LIT-101 | MV-101 is open; LIT-101 between L and H | Keep MV-101 on countinuosly; Value of LIT-101 set as 700 mm | Yes | Tank overflow
16 | 2015-12-29 22:55 | 23:03 | UV-401, AIT-502, P-501 | UV-01 is on; AIT-502 is <150; P-501 is open | Stop UV-401; Value of AIT502 set as 150; Force P-501 to remain on | Yes | Possible damage to RO | P501 could not be kept on; Reduced output at FIT-502
17 | 2015-12-30 01:43 | 1:54 | P-602, DIT-301, MV-302 | DPIT-301 is <0.4 bar; MV-302 is on; P-602 is closed | Value of DPIT-301 set to >0.4 bar; Keep MV-302 open; Keep P-602 closed | Yes | System freeze
18 | 2015-12-30 09:51 | 9:56 | P-203, P-205 | P-203 is on; P-205 is on | Turn of P-203 and P-205 | Yes | Change in water quality | Not much impact made due to closure of P-101 because tank T-101 became full
19 | 2015-12-30 10:02 | 10:12 | LIT-401, P-401 | Value of LIT-401 <1000; P-402 is on | Set value of LIT-401 as 1000; P402 is kept on | Yes | Tank underflow
20 | 2015-12-30 17:05 | 17:29 | P-101, LIT-301 | P-101 is off; P-102 is on; LIT-301 is between L and H | P-101 is turned on continuosly; Set value of LIT-301 as 801 mm | Yes | Tank 101 underflow; Tank 301 overflow
21 | 2015-12-31 01:17 | 1:45 | P-302, LIT-401 | P302 is on, LIT401 Is between L and H | Keep P-302 on contineoulsy; Value of LIT401 set as 600 mm till 1:26:01 | Yes | Tank overflow
22 | 2015-12-31 01:45 | 11:15 | P-302 | P302 is on | Close P-302 | Yes | Stop inflow of tank T-401
23 | 2015-12-31 15:32 | 15:34 | P-201, P-203, P-205 | P-201 is closed; P-203 is closed; P-205 is closed | Turn on P-201; Turn on P-203; Turn on P-205 | Yes | Wastage of chemicals | The three dosing pump did not start because of some mechanical interlock
24 | 2015-12-31 15:48 | 16:07 | LIT-101, P-101, MV-201 | P-101 is off; MV-101 is off; MV-201 is off; LIT-101 is between L and H; LIT-301 is between L and H | Turn P-101 on continuously; Turn MV-101 on continuously; Set value of LIT-101 as 700 mm; P-102 started itself because LIT301 level became low | Yes | Tank 101 underflow; Tank 301 overflow
25 | 2015-12-31 22:06 | 22:12 | LIT-401 | Water level between L and H | Set LIT-401 to less than L | No | Tank overflow
26 | 2016-01-01 10:36 | 10:46 | LIT-301 | Water level between L and H | Set LIT-301 to above HH | No | Tank underflow; Damage P-302
27 | 2016-01-01 14:21 | 14:29 | LIT-101 | Water level between L and H | Set LIT-101 to above H | No | Tank underflow; Damage P-101
28 | 2016-01-01 17:13 | 17:14 | P-101 | P-101 is on | Turn P-101 off | Yes | Stops outflow | Outflow did not stop because the system turned on P-102
29 | 2016-01-01 17:19 | 17:27 | P-101; P-102 | P-101 is on; P-102 is off | Turn P-101 off; Keep P-102 off | Yes | Stops outflow
30 | 2016-01-01 22:16 | 22:25 | LIT-101 | Water level between L and H | Set LIT-101 to less than LL | No | Tank overflow
31 | 2015-01-02 11:17 | 11:25 | P-501, FIT-502 | P-501 is on; FIT-502 in normal range | Close P-501; Set value of FIT-502 to 1.29 at 11:18:36 | No | Reduced output | P-501 did not turn off; FIT-502 decreased to 0.8; Speed of P-501 increased to 28.50 Hz from 10 Hz during attack.
32 | 2015-01-02 11:32 | 11:36 | AIT-402, AIT-502 | In Normal Range | Set value of AIT402 as 260; Set value of AIT502 to 260 | No | Water goes to drain because of overdosing | Water did not go to the drain
33 | 2015-01-02 11:44 | 11:50 | FIT-401, AIT-502 | In Normal Range | Set value of FIT-401 as 0.5; Set value of AIT-502 as 140 mV | No | UV will shut down and water will go to RO | UV did not shutdown
34 | 2015-01-02 11:52 | 11:57 | FIT-401 | In Normal Range | Set value of FIT-401 as 0 | No | UV will shut down and water will go to RO | P-402 did not close, both should be interlinked
35 | 2015-01-02 13:13 | 13:41 | LIT-301 | Water level between L and H | decrease value by 0.5 mm per second | No | Tank overflow | Rate of decrease in water level reduced after 1:33:25 PM
Single Stage Single Point Attacks
Single Stage Multi Point Attacks
Multi Stage Single Point Attacks
Multi Stage Multi Point Attacks
We changed the value to constant in 26. ICS2 stopped showing the value because it was not changing. When we stopped the attack, it interpolated the points in between. It should have shown a steep increase in level. They will not detect attacks where value is constant

## Sheet2
Attack # | Start Time | End Time | Attack Point | Attack | Violated Rules
1 | 2015-12-28 10:29 | 10:45 | MV-101 | Open MV-101 | FIT201>=2.002562999725342 and FIT101>=1.065560519695282 and P101=2 ---> MV201=2 and MV101=2"
2 | 2015-12-28 10:51 | 10:58 | P-102 | Turn on P-102
3 | 2015-12-28 11:22 | 11:28 | LIT-101 | Increase by 1 mm every second
4 | 2015-12-28 11:48 | 11:54 | MV-504 | Open MV-504
5 | 2015-12-28 11:58 |  | No Physical Impact Attack
6 | 2015-12-28 12:01 | 12:04 | AIT-202 | Set value of AIT-202 as 6
7 | 2015-12-28 12:08 | 12:16 | LIT-301 | Water level increased above HH
8 | 2015-12-28 13:10 | 13:26 | DPIT-301 | Set value of DPIT as >40kpa
9 | 2015-12-28 14:15 |  | No Physical Impact Attack
10 | 2015-12-28 14:16 | 14:19 | FIT-401 | Set value of FIT-401 as <0.7
11 | 2015-12-28 14:19 | 14:28 | FIT-401 | Set value of FIT-401 as 0
12 | 2015-12-29 11:11 |  | No Physical Impact Attack
13 | 2015-12-29 11:11 | 11:15 | MV-304 | Close MV-304
14 | 2015-12-29 11:36 | 11:43 | Mv-303 | Do not let MV-303 open
15 | 2015-12-29 11:52 |  | No Physical Impact Attack
16 | 2015-12-29 11:57 | 12:02 | LIT-301 | Decrease water level by 1mm each second
17 | 2015-12-29 14:38 | 14:50 | MV-303 | Do not let MV-303 open
18 | 2015-12-29 18:09 |  | No Physical Impact Attack
19 | 2015-12-29 18:11 | 18:15 | AIT-504 | Set value of AIT-504 to 16 uS/cm
20 | 2015-12-29 18:16 | 18:22 | AIT-504 | Set value of AIT-504 to 255 uS/cm
21 | 2015-12-29 18:30 | 18:42 | MV-101, LIT-101 | Keep MV-101 on countinuosly; Value of LIT-101 set as 700 mm
22 | 2015-12-29 22:55 | 23:03 | UV-401, AIT-502, P-501 | Stop UV-401; Value of AIT502 set as 150; Force P-501 to remain on
23 | 2015-12-30 01:43 | 1:54 | P-602, DIT-301, MV-302 | Value of DPIT-301 set to >0.4 bar; Keep MV-302 open; Keep P-602 closed
24 | 2015-12-30 09:51 | 9:56 | P-203, P-205 | Turn of P-203 and P-205
25 | 2015-12-30 10:02 | 10:12 | LIT-401, P-401 | Set value of LIT-401 as 1000; P402 is kept on
26 | 2015-12-30 17:05 | 17:29 | P-101, LIT-301 | P-101 is turned on continuosly; Set value of LIT-301 as 801 mm
27 | 2015-12-31 01:17 | 1:45 | P-302, LIT-401 | Keep P-302 on contineoulsy; Value of LIT401 set as 600 mm till 1:26:01
28 | 2015-12-31 01:45 | 11:15 | P-302 | Close P-302
29 | 2015-12-31 15:32 | 15:34 | P-201, P-203, P-205 | Turn on P-201; Turn on P-203; Turn on P-205
30 | 2015-12-31 15:48 | 16:07 | LIT-101, P-101, MV-201 | Turn P-101 on continuously; Turn MV-101 on continuously; Set value of LIT-101 as 700 mm; P-102 started itself because LIT301 level became low
31 | 2015-12-31 22:06 | 22:12 | LIT-401 | Set LIT-401 to less than L
32 | 2016-01-01 10:36 | 10:46 | LIT-301 | Set LIT-301 to above HH
33 | 2016-01-01 14:21 | 14:29 | LIT-101 | Set LIT-101 to above H
34 | 2016-01-01 17:13 | 17:14 | P-101 | Turn P-101 off
35 | 2016-01-01 17:19 | 17:27 | P-101; P-102 | Turn P-101 off; Keep P-102 off
36 | 2016-01-01 22:16 | 22:25 | LIT-101 | Set LIT-101 to less than LL
37 | 2015-01-02 11:17 | 11:25 | P-501, FIT-502 | Close P-501; Set value of FIT-502 to 1.29 at 11:18:36
38 | 2015-01-02 11:32 | 11:36 | AIT-402, AIT-502 | Set value of AIT402 as 260; Set value of AIT502 to 260
39 | 2015-01-02 11:44 | 11:50 | FIT-401, AIT-502 | Set value of FIT-401 as 0.5; Set value of AIT-502 as 140 mV
40 | 2015-01-02 11:52 | 11:57 | FIT-401 | Set value of FIT-401 as 0
41 | 2015-01-02 13:13 | 13:41 | LIT-301 | decrease value by 0.5 mm per second